{"text_format":"1","workbook":"xls","n_sheets":2,"sheets":["INFO","TLU-01"],"not_rendered":{"charts":1,"images":2,"macros":0,"external_links":1,"defined_names":3,"comments":33,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"INFO","index":0,"n_rows":42,"n_cols":11,"rows_kept":42,"cut":false,"hidden":false,"merged":[[4,0,5,9],[4,10,4,11],[5,10,5,11],[7,0,7,11],[8,0,11,11],[13,0,13,11],[14,0,35,11],[37,0,37,11],[38,0,38,11],[40,0,40,11],[41,0,42,11]],"flags":["formulas_cached_only"]}
[]
[]
[]
[]
["Návrh kruhových tlumičů GD / GDE",null,null,null,null,null,null,null,null,null,"1.0"]
[null,null,null,null,null,null,null,null,null,null,"2019-04-02"]
[]
["Popis výpočtu:"]
["Výpočtový program je určen pro návrh kruhových tlumičů hluku GREIF instalovaných ve vzduchotechnickém potrubí. Návrh je možné provádět pro všechny standardně vyráběné typy kruhových tlumičů GD / GDE podle směrnice ITS122-01. Výpočet je omezen na běžné konstrukční podmínky. V případě složitějších návrhů je nutné tlumič poptat."]
[]
[]
[]
[]
["Nejistota výpočtu:"]
["V září 2018 skončilo přechodné období a vešla v platnost nová, výrazně aktualizovaná norma ČSN EN ISO 9001:2016, která je základním kamenem kvality pro všechny seriózní výrobce. Hlavní změnou je mj. řízení rizik.\n\nZ těchto důvodů uvádíme s útlumem hluku skutečnou odchylku. V oblasti metrologie se nejedná o nic nového, ale u prezentování katalogových hodnot útlumů je to novinka, která od projektanta vyžaduje posouzení instalace v širších souvislostech.\n\nDůvodem je neznalost podmínek, za jakých bude tlumič pracovat. Proto je nutné, aby míru nejistoty posoudil projektant a zohlednil všechny faktory, které mají na útlum hluku vliv. Jsou to zejména neprůzvučnost a tuhost potrubí, ve kterém bude tlumič instalován, provozní podmínky, způsob měření výsledků atd. Je tedy na projektantovi, jakou míru rizika zvolí a odchylku přičte nebo odečte a v jaké velikosti. Námi prezentovaná rozšířená nejistota představuje interval, ve kterém s 95 % pravděpodobností bude ležet měřená hodnota při kombinaci zmíněných místních podmínek.\n\nJe tedy zřejmé, že kvalitní návrh tlumení vyžaduje podrobnou znalost místních podmínek a řízení rizika. Vzhledem k tomu, že jsme již na novou normu recertifikovaní, jsme samozřejmě připraveni tyto rizika minimalizovat a projektantům nabídnout pomocnou ruku při řešení a aplikaci.\n\nV podstatě se nejedná o nic nového, neboť po fyzikální stránce se takto chová každý soubor měření a nezáleží na výrobci nebo způsobu uvádění výsledků. My jako první toto aplikujeme a otevřeně nabízíme pomoc při řešení. Oporou nám jsou interní databáze měřených instalací, při kterých validujeme jednotlivé výsledky a porovnáváme účinnosti jednotlivých řešení."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Odkaz na projekční katalogy (www.greif.cz):"]
["ITS122-01 - Kruhové tlumiče hluku GD\n"]
[]
["Kontakt:"]
["Vaše připomínky na zlepšení, případně objevené chyby můžete posílat na micka@greif.cz.\nV případě, že budete potřebovat popoc s návrhem tlumičů, kontaktujte naší technickou podporu."]

{"sheet":"TLU-01","index":1,"n_rows":150,"n_cols":51,"rows_kept":150,"cut":false,"hidden":false,"merged":[[0,13,0,24],[0,26,1,40],[3,26,3,28],[4,0,5,11],[6,0,6,11],[7,0,7,11],[7,26,7,28],[9,0,9,2],[9,3,9,11],[9,13,9,16],[9,17,9,23],[10,10,10,11],[11,1,11,2],[11,4,11,10],[12,1,12,2],[12,4,12,10],[13,1,13,2],[13,4,13,10],[14,1,14,2],[14,4,14,10],[15,1,15,2],[15,4,15,10],[16,1,16,2],[16,4,16,10],[17,1,17,2],[17,4,17,10],[18,1,18,2],[18,4,18,10],[18,13,18,24],[19,1,19,2],[19,4,19,10],[19,26,19,28],[20,1,20,2],[20,4,20,10],[21,1,21,2],[21,4,21,10],[22,1,22,2],[22,4,22,10],[23,1,23,2],[23,4,23,10],[23,26,23,28],[24,1,24,2],[24,4,24,10],[24,26,24,28],[25,1,25,2],[25,4,25,10],[27,0,27,11],[31,0,31,11],[36,0,36,11],[37,0,37,2],[37,3,37,5],[37,6,37,8],[37,9,37,11],[38,0,38,2],[38,3,38,5],[38,6,38,8],[38,9,38,11],[39,0,39,2],[39,3,39,5],[39,6,39,8],[39,9,39,11],[40,0,40,8],[40,9,40,11],[146,26,146,29]],"flags":["formulas_cached_only"]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Zatlumení zdroje - koncepce výpočtu:",null,null,null,null,null,null,null,null,null,null,null,null,"Data pro návrh kruhových tlumičů"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Zadejte žlutá pole, nebo vepište poznámky…",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Korekční křivka:"]
["Návrh kruhových tlumičů GD / GDE",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"A","dB",-39.4,-26.2,-16.1,-8.6,-3.2,0,1.2,1,-1.1]
["Zadejte název projektu"]
["Zadejte název tlumiče",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hladiny hluku:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"SUM"]
["Tlaková ztráta:",null,null,0,null,null,null,null,null,null,null,null,null,"Zatlumení zdroje - výpočet:",null,null,null,"Zadejte tvar hlukového spektra (L = lineární, A = korigované)",null,null,null,null,null,null,"L",null,"LWZ-Lin","dB",75,90,100,103,99,94,84,78,74,106.20956148272913]
["dpt","=",null,null,null,null,null,null,null,null,96.20943746239055,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"A",null,"LWZ-A","dBA",35.6,63.8,83.9,94.4,95.8,94,85.2,79,72.9,99.88823949227175]
["Q",4000,null,"m3/h",0,null,null,null,null,null,null,1,null,0,"dB",75,90,100,103,99,94,84,78,74,99.88823949227175,null,"DT","dB",4,5,14,27,46,50,35,19,15,"-"]
["d",250,null,"mm",0,null,null,null,null,null,null,1,null,"DT","dB",4,5,14,27,46,50,35,19,15,"-",null,"LWT-Lin","dB",66.24437709254545,60.240984992852475,54.35557992867988,48.57982458325102,43.29897851059628,38.64233985432822,33.802856645184875,28.296544632108642,22.430113413424593,67.516820158319]
["LT",2000,null,"mm",0,null,null,null,null,null,null,1,null,0,"dB",66.24437709254545,60.240984992852475,54.35557992867988,48.57982458325102,43.29897851059628,38.64233985432822,33.802856645184875,28.296544632108642,22.430113413424593,46.165956741085346,null,"LWT-A","dBA",26.84437709254545,34.04098499285247,38.25557992867988,39.979824583251016,40.098978510596275,38.64233985432822,35.00285664518488,29.296544632108642,21.33011341342459,46.165956741085346]
["typ","GD",null,"-",0,null,null,null,null,null,null,1,null,"DP","dB",0,0,0,0,0,0,0,0,0,"-",null,"DP","dB",0,0,0,0,0,0,0,0,0,"-"]
["konec",0,null,"-",0,null,null,null,null,null,null,1,null,0,"dB",72.2532900255291,85.01449298890114,86.00297299135346,76.00785911700507,53.44197336568759,45.1100312851408,49.12929718727979,59.00369193600633,59.00095663842233,72.53122049721054,null,"LWC-Lin","dB",72.2532900255291,85.01449298890114,86.00297299135346,76.00785911700507,53.44197336568759,45.1100312851408,49.12929718727979,59.00369193600633,59.00095663842233,88.88894046074306]
["t",20,null,"°C",0,null,null,null,null,null,null,1,null,"DC","dB",2.746709974470903,4.985507011098861,13.99702700864654,26.99214088299493,45.55802663431241,48.8899687148592,34.87070281272021,18.996308063993673,14.99904336157767,27.35701899506121,null,"LWC-A","dBA",32.8532900255291,58.81449298890114,69.90297299135347,67.40785911700507,50.241973365687585,45.1100312851408,50.32929718727979,60.00369193600633,57.90095663842233,72.53122049721054]
["p",101325,null,"Pa",0,null,null,null,null,null,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DC","dB",2.746709974470903,4.985507011098861,13.99702700864654,26.99214088299493,45.55802663431241,48.8899687148592,34.87070281272021,18.996308063993673,14.99904336157767,"-"]
["res",0.2,null,"%",0,null,null,null,null,null,null,1,null,"Graf - [dB / Hz]:"]
["ro",1.2036989821185216,null,"kg/m3","hustota vzduchu",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Podmínky výběru:"]
["S",0.04908738521234052,null,"m2","plocha vstupního potrubí",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Typ","Vstup","Délka","Označení tlumiče",null,null,"Jádro","Vnější","Váha","Ksi","Cena","Příruba",31.5,63,125,250,500,1000,2000,4000,8000]
["Si",0.04908738521234052,null,"m2","volná průtočná plocha v tlumiči",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,250,2000,0,null,null,0,450,39.1,0.26,6280,610,4,5,14,27,46,50,35,19,15]
["w",22.63536968418067,null,"m/s","rychlost proudění ve vstupním potrubí před tlumičem"]
["wi",22.63536968418067,null,"m/s",0,null,null,null,null,null,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Data katalog:"]
["x",0.26,null,"-","celkový součinitel tlakové ztráty tlumiče",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Označení tlumiče",null,null,"Typ","Vstup","Jádro","Vnější","Délka","Váha","Ksi","Cena","Příruba",31.5,63,125,250,500,1000,2000,4000,8000]
["c",343.2917585669658,null,"m/s","rychlost zvuku ve vzduchu při teplotě t",null,null,null,null,null,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 100-1000",null,null,"GD",100,0,300,1000,12.5,0.5700000000000001,2190,355,5,6,18,30,38,50,50,42,24]
[null,null,null,null,null,null,null,null,null,null,null,"Výpočet je proveden na základě simulace CFD, odhad nepřesnosti ± 10%",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 125-1000",null,null,"GD",125,0,315,1000,13.5,0.36,2300,375,4,5,15,26,34,47,48,31,22]
["Vlastní hluk:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 140-1000",null,null,"GD",140,0,355,1000,16.1,0.29000000000000004,2600,395,4,5,14,25,33,46,46,29,20]
["f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"LWT-A",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 150-1000",null,null,"GD",150,0,355,1000,16.3,0.26,2760,420,4,5,13,24,32,45,44,27,18]
["LWT-Lin","dB",66.24437709254545,60.240984992852475,54.35557992867988,48.57982458325102,43.29897851059628,38.64233985432822,33.802856645184875,28.296544632108642,22.430113413424593,46.165956741085346,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 160-1000",null,null,"GD",160,0,355,1000,16.5,0.23,2895,435,4,5,11,23,31,44,42,26,15]
[null,null,null,null,null,null,null,null,null,null,null,"Nejistota výpočtu vlastního hluku ± 3 dB",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 180-1000",null,null,"GD",180,0,400,1000,18.5,0.21,3165,455,3,4,9,21,29,42,38,23,14]
["Útlum a váha kruhového tlumiče:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 200-1000",null,null,"GD",200,0,400,1000,18.8,0.18,3395,470,3,4,8,18,27,40,34,20,13]
["f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"M",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 224-1000",null,null,"GD",224,0,400,1000,18.9,0.15,3735,485,3,4,8,17,26,36,29,17,12]
["DT","dB",4,5,14,27,46,50,35,19,15,"kg/ks",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 250-1000",null,null,"GD",250,0,450,1000,21.5,0.12,4045,610,2,3,8,16,25,33,25,15,11]
["2sigR","dB",7,6,4,4,4,4,4,4,7,39.1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD280-1000",null,null,"GD",280,0,500,1000,26.1,0.11,4415,625,2,3,7,15,25,31,23,15,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 300-1000",null,null,"GD",300,0,500,1000,24.5,0.1,4630,655,2,3,7,14,24,30,22,14,9]
["Závěrečné shrnutí výsledků:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 315-1000",null,null,"GD",315,0,500,1000,24.8,0.09,4765,680,2,3,6,12,23,29,20,14,9]
["Označení tlumiče",null,null,0,null,null,"Hmotnost tlumiče",null,null,39.1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 355-1000",null,null,"GD",355,0,560,1000,28.5,0.08,5510,875,1,2,6,12,23,26,18,13,8]
["Nominální rozměr",null,null,250,null,null,"Délka aktivní části",null,null,2000,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 400-1000",null,null,"GD",400,0,600,1000,30.5,0.06,6015,1065,1,2,5,11,23,25,16,12,7]
["Vnější průměr tlumiče",null,null,450,null,null,"Celková délka tlumiče",null,null,2200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 450-1000",null,null,"GD",450,0,630,1000,32.1,0.05,7700,1320,1,2,5,11,21,23,15,10,6]
["Brutto cena tlumiče (bez DPH, EXW Uhlířské Janovice)",null,null,null,null,null,null,null,null,6280,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 500-1000",null,null,"GD",500,0,710,1000,37.5,0.04,9130,1465,1,2,4,10,20,22,14,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 560-1000",null,null,"GD",560,0,800,1000,44.1,0.04,10975,1535,1,2,4,10,18,20,14,8,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 600-1000",null,null,"GD",600,0,800,1000,43.2,0.04,11685,1575,0,1,3,9,17,17,13,7,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 630-1000",null,null,"GD",630,0,900,1000,52,0.03,12480,2010,0,1,3,8,16,14,13,7,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 710-1000",null,null,"GD",710,0,900,1000,48.1,0.03,14155,2120,0,1,2,6,14,12,11,6,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 800-1000",null,null,"GD",800,0,1000,1000,65.1,0.03,15465,2235,0,1,2,5,12,10,9,6,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 900-1000",null,null,"GD",900,0,1120,1000,75.5,0.02,18335,6200,0,0,1,3,8,9,7,2,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 1000-1000",null,null,"GD",1000,0,1250,1000,87.2,0.02,20085,8745,0,0,0,1,4,5,4,1,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 100-1500",null,null,"GD",100,0,300,1500,17.5,0.84,2925,355,5,6,22,32,46,50,50,50,30]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 125-1500",null,null,"GD",125,0,315,1500,19,0.53,3080,375,5,6,18,27,42,50,50,40,27]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 140-1500",null,null,"GD",140,0,355,1500,22.1,0.44,3335,395,5,6,17,26,41,50,47,36,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 150-1500",null,null,"GD",150,0,355,1500,22.5,0.39,3505,420,5,6,16,25,41,50,46,32,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 160-1500",null,null,"GD",160,0,355,1500,22.8,0.35,3785,435,5,6,15,24,40,50,45,27,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 180-1500",null,null,"GD",180,0,400,1500,26.1,0.31,4175,455,4,5,13,22,38,49,40,24,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 200-1500",null,null,"GD",200,0,400,1500,26.3,0.27,4410,470,4,5,11,21,37,48,35,22,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 224-1500",null,null,"GD",224,0,400,1500,26.5,0.22,4865,485,3,4,11,21,37,44,31,18,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 250-1500",null,null,"GD",250,0,450,1500,30.5,0.19,5190,610,3,4,11,21,37,41,27,15,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 280-1500",null,null,"GD",280,0,500,1500,35.1,0.16,5660,625,3,4,11,19,34,41,25,15,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 300-1500",null,null,"GD",300,0,500,1500,34.5,0.14,5990,655,2,3,10,17,31,41,24,14,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 315-1500",null,null,"GD",315,0,500,1500,34.8,0.13,6170,680,2,3,9,16,31,41,23,14,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 355-1500",null,null,"GD",355,0,560,1500,40.2,0.11,7155,875,2,3,8,15,30,36,19,13,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 400-1500",null,null,"GD",400,0,600,1500,43.1,0.09,7705,1065,2,3,7,15,30,31,16,12,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 450-1500",null,null,"GD",450,0,630,1500,45.1,0.08,9590,1320,1,2,6,15,30,29,15,10,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 500-1500",null,null,"GD",500,0,710,1500,53.1,0.06,11165,1465,1,2,6,14,29,27,14,8,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 560-1500",null,null,"GD",560,0,800,1500,62,0.06,13250,1535,1,2,5,14,29,25,14,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 600-1500",null,null,"GD",600,0,800,1500,65,0.06,14430,1575,1,2,5,13,28,24,13,7,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 630-1500",null,null,"GD",630,0,900,1500,73.5,0.04,15300,2010,1,2,5,12,28,23,13,7,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 710-1500",null,null,"GD",710,0,900,1500,68.2,0.04,17140,2120,1,2,4,11,27,21,11,6,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 800-1500",null,null,"GD",800,0,1000,1500,91.2,0.04,18790,2235,1,2,4,11,26,20,9,6,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 900-1500",null,null,"GD",900,0,1120,1500,105.5,0.03,24310,6200,0,1,3,8,20,16,6,4,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 1000-1500",null,null,"GD",1000,0,1250,1500,121.5,0.03,26470,8745,0,0,1,4,10,8,3,2,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 100-2000",null,null,"GD",100,0,300,2000,23,1.13,3630,355,6,7,28,41,50,50,50,50,39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 125-2000",null,null,"GD",125,0,315,2000,24.5,0.72,3835,375,6,7,23,35,50,50,50,50,35]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 140-2000",null,null,"GD",140,0,355,2000,29.1,0.5800000000000001,4095,395,6,7,21,33,50,50,50,45,31]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 150-2000",null,null,"GD",150,0,355,2000,29.3,0.52,4415,420,6,7,20,32,50,50,50,40,28]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 160-2000",null,null,"GD",160,0,355,2000,29.5,0.48,4635,435,6,7,19,31,50,50,50,35,24]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 180-2000",null,null,"GD",180,0,400,2000,34.1,0.41,5085,455,5,6,17,29,48,50,47,31,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 200-2000",null,null,"GD",200,0,400,2000,34.5,0.35,5375,470,5,6,16,27,48,50,45,28,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 224-2000",null,null,"GD",224,0,400,2000,35.5,0.29000000000000004,5875,485,4,5,15,27,47,50,37,23,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 250-2000",null,null,"GD",250,0,450,2000,39.1,0.26,6280,610,4,5,14,27,46,50,35,19,15]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 280-2000",null,null,"GD",280,0,500,2000,45.1,0.21,6785,625,4,5,13,25,44,50,33,17,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 300-2000",null,null,"GD",300,0,500,2000,44.5,0.19,7155,655,3,4,12,24,43,50,31,16,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 315-2000",null,null,"GD",315,0,500,2000,44.8,0.18,7510,680,3,4,11,23,42,50,29,15,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 355-2000",null,null,"GD",355,0,560,2000,51.5,0.15,8605,875,3,4,10,21,41,45,24,14,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 400-2000",null,null,"GD",400,0,600,2000,55.5,0.13,9390,1065,2,3,9,20,41,40,20,13,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 450-2000",null,null,"GD",450,0,630,2000,58.1,0.11,11325,1320,2,3,8,19,40,37,19,11,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 500-2000",null,null,"GD",500,0,710,2000,68.2,0.08,13200,1465,1,2,7,18,39,35,19,9,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 560-2000",null,null,"GD",560,0,800,2000,80.3,0.08,15845,1535,1,2,7,17,38,33,17,9,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 600-2000",null,null,"GD",600,0,800,2000,87.5,0.08,17235,1575,1,2,6,16,37,31,16,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 630-2000",null,null,"GD",630,0,900,2000,94.2,0.05,18135,2010,1,2,6,15,36,29,14,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 710-2000",null,null,"GD",710,0,900,2000,97.5,0.05,20390,2120,1,2,6,14,34,27,12,7,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 800-2000",null,null,"GD",800,0,1000,2000,117.2,0.05,22135,2235,1,2,5,14,33,26,10,6,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 900-2000",null,null,"GD",900,0,1120,2000,135.1,0.04,30180,6200,0,1,4,10,23,18,8,5,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 1000-2000",null,null,"GD",1000,0,1250,2000,156.6,0.04,32855,8745,0,1,2,5,12,9,4,3,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 200-1000",null,null,"GDE",200,120,400,1000,25.1,1.46,4005,470,6,7,12,22,40,50,50,50,46]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 224-1000",null,null,"GDE",224,120,400,1000,25.5,0.87,4415,485,5,6,11,19,35,48,50,50,41]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 250-1000",null,null,"GDE",250,120,450,1000,29.2,0.5700000000000001,4685,610,4,5,10,17,30,47,50,50,36]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 280-1000",null,null,"GDE",280,190,500,1000,34.5,2.28,5185,625,4,5,10,16,29,46,48,47,33]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 300-1000",null,null,"GDE",300,190,500,1000,34.6,1.53,5490,655,3,4,9,15,28,45,46,44,30]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 315-1000",null,null,"GDE",315,190,500,1000,34.8,1.4,5710,680,3,4,9,15,27,44,45,39,27]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 355-1000",null,null,"GDE",355,240,560,1000,39.5,2.44,6555,875,3,4,8,14,26,43,42,34,24]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 400-1000",null,null,"GDE",400,240,600,1000,43.5,1.12,7155,1065,3,3,7,13,25,40,38,29,21]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 450-1000",null,null,"GDE",450,290,630,1000,47,1.51,9050,1320,2,3,7,12,24,39,35,26,18]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 500-1000",null,null,"GDE",500,290,710,1000,55.1,0.96,10535,1465,1,2,6,12,23,38,33,24,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 560-1000",null,null,"GDE",560,390,800,1000,66.1,2.42,13240,1535,1,2,6,11,22,36,31,21,15]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 600-1000",null,null,"GDE",600,390,800,1000,64.5,1.45,13985,1575,1,2,5,11,21,35,30,20,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 630-1000",null,null,"GDE",630,390,900,1000,75,1.45,14590,2010,1,2,5,11,21,34,29,19,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 710-1000",null,null,"GDE",710,390,900,1000,81.5,0.52,16650,2120,1,2,4,10,20,30,22,14,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 800-1000",null,null,"GDE",800,490,1000,1000,94.5,1.13,18215,2235,1,2,2,8,15,24,18,10,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 900-1000",null,null,"GDE",900,590,1120,1000,109.5,1.21,25235,6200,1,1,2,7,12,20,15,8,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 1000-1000",null,null,"GDE",1000,690,1250,1000,125.5,2.14,29355,8745,1,1,1,6,10,15,10,6,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 200-1500",null,null,"GDE",200,120,400,1500,35.5,2.01,5245,470,8,9,16,26,45,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 224-1500",null,null,"GDE",224,120,400,1500,35.8,1.36,5660,485,7,8,15,24,42,50,50,50,47]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 250-1500",null,null,"GDE",250,120,450,1500,40.5,0.83,6035,610,6,7,14,22,41,50,50,50,44]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 280-1500",null,null,"GDE",280,190,500,1500,48.5,2.78,6735,625,6,7,14,21,39,50,50,50,40]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 300-1500",null,null,"GDE",300,190,500,1500,48.6,1.75,7040,655,6,7,13,20,38,50,50,50,37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 315-1500",null,null,"GDE",315,190,500,1500,48.8,1.49,7430,680,6,7,12,20,37,50,50,50,34]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 355-1500",null,null,"GDE",355,240,560,1500,55,2.74,8480,875,5,6,11,18,34,50,50,45,30]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 400-1500",null,null,"GDE",400,240,600,1500,61.1,1.21,9310,1065,5,6,10,17,33,50,50,40,26]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 450-1500",null,null,"GDE",450,290,630,1500,66.3,1.83,11325,1320,4,5,9,16,31,50,50,36,23]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 500-1500",null,null,"GDE",500,290,710,1500,76.2,1.22,13145,1465,4,5,9,16,30,50,50,33,21]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 560-1500",null,null,"GDE",560,390,800,1500,93.5,2.71,15845,1535,3,4,8,15,30,50,48,29,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 600-1500",null,null,"GDE",600,390,800,1500,97,1.56,17195,1575,3,4,8,14,29,50,46,27,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 630-1500",null,null,"GDE",630,390,900,1500,106.2,1.56,18195,2010,3,4,8,14,29,50,44,26,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 710-1500",null,null,"GDE",710,390,900,1500,110.5,0.79,20390,2120,3,4,7,13,28,50,41,23,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 800-1500",null,null,"GDE",800,490,1000,1500,133.5,1.26,22540,2235,2,3,6,13,26,49,37,20,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 900-1500",null,null,"GDE",900,590,1120,1500,156.2,1.84,33580,6200,2,2,4,10,20,39,29,16,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 1000-1500",null,null,"GDE",1000,690,1250,1500,181.5,2.31,38935,8745,1,2,3,6,10,19,14,8,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 200-2000",null,null,"GDE",200,120,400,2000,45,2.5,6495,470,9,10,19,31,50,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 224-2000",null,null,"GDE",224,120,400,2000,45.4,1.78,7010,485,8,9,18,28,50,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 250-2000",null,null,"GDE",250,120,450,2000,52.2,1.05,7360,610,7,8,17,26,49,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 280-2000",null,null,"GDE",280,190,500,2000,62.5,3.25,8285,625,7,8,17,25,46,50,50,50,48]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 300-2000",null,null,"GDE",300,190,500,2000,62.7,1.97,8810,655,7,8,15,24,45,50,50,50,44]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 315-2000",null,null,"GDE",315,190,500,2000,62.9,1.57,9130,680,7,8,14,24,44,50,50,50,40]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 355-2000",null,null,"GDE",355,240,560,2000,70.5,3,10440,875,6,7,13,21,40,50,50,50,36]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 400-2000",null,null,"GDE",400,240,600,2000,78.5,1.28,11455,1065,6,7,12,20,39,50,50,48,31]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 450-2000",null,null,"GDE",450,290,630,2000,85.5,2.11,13910,1320,5,6,11,19,37,50,50,43,27]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 500-2000",null,null,"GDE",500,290,710,2000,98.1,1.48,15725,1465,5,6,11,19,36,50,50,39,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 560-2000",null,null,"GDE",560,390,800,2000,120.5,2.97,19165,1535,4,5,10,18,36,50,50,35,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 600-2000",null,null,"GDE",600,390,800,2000,127.5,1.67,20745,1575,4,5,10,17,35,50,50,32,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 630-2000",null,null,"GDE",630,390,900,2000,137,1.67,21785,2010,4,5,10,17,35,50,50,31,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 710-2000",null,null,"GDE",710,390,900,2000,139.5,1.02,24430,2120,3,4,8,15,33,50,49,28,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 800-2000",null,null,"GDE",800,490,1000,2000,172.5,1.44,26845,2235,3,4,7,15,31,50,44,24,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 900-2000",null,null,"GDE",900,590,1120,2000,202.5,2.21,41920,6200,3,4,7,14,29,50,41,20,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 1000-2000",null,null,"GDE",1000,690,1250,2000,237,2.63,48515,8745,3,4,7,13,27,50,40,19,12]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Vlastní hluk - typy GD / GDE"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Q","d","dj","t","p","typ","S","Si","w","wi","c","Ma","H","delta","Wo","B",31.5,63,125,250,500,1000,2000,4000,8000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m3/h","mm","mm","°C","Pa","-","m2","m2","m/s","m/s","m/s","m/s","m","-","W","-","dB","dB","dB","dB","dB","dB","dB","dB","dB"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4000,250,0,20,101325,0,0.04908738521234052,0.04908738521234052,22.63536968418067,22.63536968418067,343.2917585669658,0.06593624553840023,0.25,0.02,1,48,66.24437709254545,60.240984992852475,54.35557992867988,48.57982458325102,43.29897851059628,38.64233985432822,33.802856645184875,28.296544632108642,22.430113413424593]