{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["INFO","TLU-01"],"not_rendered":{"charts":1,"images":1,"macros":0,"external_links":0,"defined_names":1,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"INFO","index":0,"n_rows":42,"n_cols":11,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,10,0,11],[41,0,42,11],[7,0,7,11],[14,0,35,11],[38,0,38,11],[37,0,37,11],[13,0,13,11],[4,0,5,9],[1,10,1,11],[2,10,2,11],[8,0,11,11],[40,0,40,11]]}
[null,null,null,null,null,null,null,null,null,null,"Q199-02"]
[null,null,null,null,null,null,null,null,null,null,"Verze: 5.0"]
[null,null,null,null,null,null,null,null,null,null,"2026-03-13"]
[]
["Návrh kruhových tlumičů GD / GDE"]
[]
[]
["Popis výpočtu:"]
["Výpočtový program je určen pro návrh kruhových tlumičů hluku GREIF instalovaných ve vzduchotechnickém potrubí. Návrh je možné provádět pro všechny standardně vyráběné typy kruhových tlumičů GD / GDE podle směrnice ITS122-01. Výpočet je omezen na běžné konstrukční podmínky. V případě složitějších návrhů je nutné tlumič poptat.\nUvedené ceny jsou orientační. Skutečná cena včetně obchodních podmínek bude stanovena na základě nabídky."]
[]
[]
[]
[]
["Nejistota výpočtu:"]
["V září 2018 skončilo přechodné období a vešla v platnost nová, výrazně aktualizovaná norma ČSN EN ISO 9001:2016, která je základním kamenem kvality pro všechny seriózní výrobce. Hlavní změnou je mj. řízení rizik.\n\nZ těchto důvodů uvádíme s útlumem hluku skutečnou odchylku. V oblasti metrologie se nejedná o nic nového, ale u prezentování katalogových hodnot útlumů je to novinka, která od projektanta vyžaduje posouzení instalace v širších souvislostech.\n\nDůvodem je neznalost podmínek, za jakých bude tlumič pracovat. Proto je nutné, aby míru nejistoty posoudil projektant a zohlednil všechny faktory, které mají na útlum hluku vliv. Jsou to zejména neprůzvučnost a tuhost potrubí, ve kterém bude tlumič instalován, provozní podmínky, způsob měření výsledků atd. Je tedy na projektantovi, jakou míru rizika zvolí a odchylku přičte nebo odečte a v jaké velikosti. Námi prezentovaná rozšířená nejistota představuje interval, ve kterém s 95 % pravděpodobností bude ležet měřená hodnota při kombinaci zmíněných místních podmínek.\n\nJe tedy zřejmé, že kvalitní návrh tlumení vyžaduje podrobnou znalost místních podmínek a řízení rizika. Vzhledem k tomu, že jsme již na novou normu recertifikovaní, jsme samozřejmě připraveni tyto rizika minimalizovat a projektantům nabídnout pomocnou ruku při řešení a aplikaci.\n\nV podstatě se nejedná o nic nového, neboť po fyzikální stránce se takto chová každý soubor měření a nezáleží na výrobci nebo způsobu uvádění výsledků. My jako první toto aplikujeme a otevřeně nabízíme pomoc při řešení. Oporou nám jsou interní databáze měřených instalací, při kterých validujeme jednotlivé výsledky a porovnáváme účinnosti jednotlivých řešení."]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Odkaz na projekční katalogy (www.greif.cz):"]
["ITS122-01 - Kruhové tlumiče hluku GD\n"]
[]
["Kontakt:"]
["Vaše připomínky na zlepšení, případně objevené chyby můžete posílat na micka@greif.cz.\nV případě, že budete potřebovat pomoc s návrhem tlumičů, kontaktujte naší technickou podporu."]

{"sheet":"TLU-01","index":1,"n_rows":154,"n_cols":51,"rows_kept":154,"cut":false,"hidden":false,"merged":[[153,27,153,28],[153,29,153,50],[40,9,40,11],[38,6,38,8],[37,6,37,8],[38,9,38,11],[37,9,37,11],[39,9,39,11],[38,3,38,5],[37,3,37,5],[38,0,38,2],[37,0,37,2],[40,0,40,8],[39,6,39,8],[39,0,39,2],[39,3,39,5],[17,1,17,2],[11,4,11,10],[12,1,12,2],[21,4,21,10],[21,1,21,2],[13,1,13,2],[14,1,14,2],[17,4,17,10],[20,1,20,2],[20,4,20,10],[18,4,18,10],[18,1,18,2],[19,4,19,10],[15,1,15,2],[15,4,15,10],[0,13,0,24],[6,0,6,11],[7,0,7,11],[16,1,16,2],[10,10,10,11],[11,1,11,2],[4,0,5,11],[9,13,9,16],[9,17,9,23],[9,0,9,2],[9,3,9,11],[13,4,13,10],[14,4,14,10],[16,4,16,10],[12,4,12,10],[2,13,5,14],[19,1,19,2],[31,0,31,11],[36,0,36,11],[18,13,18,24],[23,4,23,10],[24,4,24,10],[25,4,25,10],[24,1,24,2],[25,1,25,2],[27,0,27,11],[22,1,22,2],[23,1,23,2],[23,26,23,28],[24,26,24,28],[3,26,3,28],[7,26,7,28],[22,4,22,10],[1,8,2,11],[152,29,152,50],[6,13,7,14],[6,15,7,22],[6,23,7,24],[151,26,151,28],[152,27,152,28],[146,26,146,29],[2,16,5,17],[2,20,5,21],[2,23,5,24],[3,15,4,15],[3,18,4,19],[3,22,4,22],[0,26,1,40],[19,26,19,28]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Zatlumení zdroje - koncepce výpočtu:",null,null,null,null,null,null,null,null,null,null,null,null,"Data pro návrh kruhových tlumičů"]
[null,null,null,null,null,null,null,null,"Zadejte označení výpočtu"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"ZDROJ\nHLUKU\nLWZ",null,null,"ÚTLUM HLUKU\nTLUMIČEM\nDT, LWT",null,null,null,"ÚTLUM HLUKU\nPOTRUBÍM\nDP",null,null,"VÝSLEDNÝ\nÚTLUM HLUKU\nDC, LWC"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"→",null,null,"→",null,null,null,"→",null,null,null,"Korekční křivka"]
["Návrh kruhových tlumičů GD / GDE",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"A","dB",-39.4,-26.2,-16.100000000000001,-8.6,-3.2,0,1.2,1,-1.1000000000000001]
["Zadejte název projektu",null,null,null,null,null,null,null,null,null,null,null,null,"| ←",null,"CELKOVÝ ÚTLUM HLUKU DC = LWZ - LWC",null,null,null,null,null,null,null,"→ |"]
["Zadejte název tlumiče",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hladiny hluku"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"SUM"]
["Tlaková ztráta:",null,null,{"$f":"IF($L$26=1,\"Zadejte žlutá pole, nebo vepište poznámky…\",\"Zadejte správné hodnoty...\")","v":"Zadejte žlutá pole, nebo vepište poznámky…"},null,null,null,null,null,null,null,null,null,"Zatlumení zdroje - výpočet:",null,null,null,"Zadejte tvar hlukového spektra (L = lineární, A = korigované)",null,null,null,null,null,null,"L",null,"LWZ-Lin","dB",{"$f":"IF($Y$10=\"L\",P12,IF($Y$10=\"A\",IF((P12-AC6)<0,0,P12-AC6)))","v":75},90,100,103,99,94,84,78,74,{"$f":"IF(10*LOG10((10^(AC10/10))+(10^(AD10/10))+(10^(AE10/10))+(10^(AF10/10))+(10^(AG10/10))+(10^(AH10/10))+(10^(AI10/10))+(10^(AJ10/10))+(10^(AK10/10)))<20,\"<20\",10*LOG10((10^(AC10/10))+(10^(AD10/10))+(10^(AE10/10))+(10^(AF10/10))+(10^(AG10/10))+(10^(AH10/10))+(10^(AI10/10))+(10^(AJ10/10))+(10^(AK10/10))))","v":106.20956148272913}]
["dpt","=",null,null,null,null,null,null,null,null,{"$f":"IF(L26=0,\"\",(0.5*$B$20*$B$23^2*$B$25)*(1+B19))","v":41.290931270576415},null,null,"f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"A",null,"LWZ-A","dBA",{"$f":"IF($Y$10=\"A\",P12,IF($Y$10=\"L\",IF((P12+AC6)<0,0,P12+AC6)))","v":35.6},63.8,83.9,94.4,95.8,94,85.2,79,72.900000000000006,{"$f":"IF(10*LOG10((10^(AC11/10))+(10^(AD11/10))+(10^(AE11/10))+(10^(AF11/10))+(10^(AG11/10))+(10^(AH11/10))+(10^(AI11/10))+(10^(AJ11/10))+(10^(AK11/10)))<20,\"<20\",10*LOG10((10^(AC11/10))+(10^(AD11/10))+(10^(AE11/10))+(10^(AF11/10))+(10^(AG11/10))+(10^(AH11/10))+(10^(AI11/10))+(10^(AJ11/10))+(10^(AK11/10))))","v":99.888239492271751}]
["Q",5000,null,"m3/h",{"$f":"IF(L12=1,\"celkový průtok vzduchu tlumičem\",\"zadejte průtok větší než 0 m3/h\")","v":"celkový průtok vzduchu tlumičem"},null,null,null,null,null,null,{"$f":"IF(B12<=0,0,1)","v":1},null,{"$f":"IF($Y$10=\"L\",\"LWZ-Lin\",IF($Y$10=\"A\",\"LWZ-A\",\"\"))","v":"LWZ-Lin"},"dB",75,90,100,103,99,94,84,78,74,{"$f":"AL11","v":99.888239492271751},null,"DT","dB",{"$f":"IF($L$26=0,\"\",AM22)","v":3},{"$f":"IF($L$26=0,\"\",AN22)","v":4},11,23,42,50,29,15,10,"-"]
["d",315,null,"mm",{"$f":"IF(L13=1,\"nominální průměr tlumiče\",\"zadejte správný nominální průměr - rozlišujte GD a GDE\")","v":"nominální průměr tlumiče"},null,null,null,null,null,null,{"$f":"IF(ISERR(DGET(AA25:AU145,\"Vstup\",AA21:AC22)),0,1)","v":1},null,"DT","dB",{"$f":"C34","v":3},4,11,23,42,50,29,15,10,"-",null,"LWT-Lin","dB",{"$f":"IF($L$26=0,0,IF(AQ150<0,0,AQ150))","v":60.017808874809965},{"$f":"IF($L$26=0,0,IF(AR150<0,0,AR150))","v":54.024157806065745},48.174854457459034,42.516726589776809,37.459647612648638,32.837806092016933,27.750971269105303,22.075328168559288,16.15177873892668,{"$f":"IF(10*LOG10((10^(AC13/10))+(10^(AD13/10))+(10^(AE13/10))+(10^(AF13/10))+(10^(AG13/10))+(10^(AH13/10))+(10^(AI13/10))+(10^(AJ13/10))+(10^(AK13/10)))<20,\"<20\",10*LOG10((10^(AC13/10))+(10^(AD13/10))+(10^(AE13/10))+(10^(AF13/10))+(10^(AG13/10))+(10^(AH13/10))+(10^(AI13/10))+(10^(AJ13/10))+(10^(AK13/10))))","v":61.298606071063055}]
["LT",2000,null,"mm",{"$f":"IF(L14=1,\"délka tlumiče (1000, 1500 nebo 2000), atypy na vyžádání\",\"zadejte správnou délku tlumiče 1000, 1500 nebo 2000 mm\")","v":"délka tlumiče (1000, 1500 nebo 2000), atypy na vyžádání"},null,null,null,null,null,null,{"$f":"IF(OR(B14=1000,B14=1500,B14=2000),1,0)","v":1},null,{"$f":"IF($Y$10=\"L\",\"LWT-Lin\",IF($Y$10=\"A\",\"LWT-A\",\"\"))","v":"LWT-Lin"},"dB",{"$f":"IF($L$26=0,\"\",IF($Y$10=\"L\",AC13,IF($Y$10=\"A\",AC14,\"\")))","v":60.017808874809965},54.024157806065745,48.174854457459034,42.516726589776809,37.459647612648638,32.837806092016933,27.750971269105303,22.075328168559288,16.15177873892668,{"$f":"IF($L$26=0,\"\",AL14)","v":40.173267824161492},null,"LWT-A","dBA",{"$f":"IF($L$26=0,0,IF((AC13+AC6)<0,0,AC13+AC6))","v":20.617808874809967},27.824157806065745,32.074854457459033,33.916726589776808,34.259647612648635,32.837806092016933,28.950971269105302,23.075328168559288,15.05177873892668,{"$f":"IF(10*LOG10((10^(AC14/10))+(10^(AD14/10))+(10^(AE14/10))+(10^(AF14/10))+(10^(AG14/10))+(10^(AH14/10))+(10^(AI14/10))+(10^(AJ14/10))+(10^(AK14/10)))<20,\"<20\",10*LOG10((10^(AC14/10))+(10^(AD14/10))+(10^(AE14/10))+(10^(AF14/10))+(10^(AG14/10))+(10^(AH14/10))+(10^(AI14/10))+(10^(AJ14/10))+(10^(AK14/10))))","v":40.173267824161492}]
["typ","GD",null,"-",{"$f":"IF(L15=1,\"zadejte typ tlumiče GD nebo GDE\",\"chybný typ tlumiče\")","v":"zadejte typ tlumiče GD nebo GDE"},null,null,null,null,null,null,{"$f":"IF(OR(B15=\"GD\",B15=\"GDE\"),1,0)","v":1},null,"DP","dB",0,0,0,0,0,0,0,0,0,"-",null,"DP","dB",{"$f":"P15","v":0},0,0,0,0,0,0,0,0,"-"]
["konec",0,null,"-",{"$f":"IF(L16=1,\"provedení připojení tlumiče na potrubí\",\"zadejte správné zakončení tlumiče: 0, 1 nebo 2\")","v":"provedení připojení tlumiče na potrubí"},null,null,null,null,null,null,{"$f":"IF(B16=\"\",0,IF(OR(B16=0,B16=1,B16=2),1,0))","v":1},null,{"$f":"IF($Y$10=\"L\",\"LWC-Lin\",IF($Y$10=\"A\",\"LWC-A\",\"\"))","v":"LWC-Lin"},"dB",{"$f":"IF($L$26=0,\"\",IF($Y$10=\"L\",AC16,IF($Y$10=\"A\",AC17,\"\")))","v":72.266782770449126},86.002754624167494,89.000359130095035,80.00077520793468,57.048011611194525,44.320225041797052,55.008174715335123,63.000350993907688,64.000071278511427,{"$f":"IF($L$26=0,\"\",AL17)","v":75.956407112696496},null,"LWC-Lin","dB",{"$f":"IF($L$26=0,0,IF(10*LOG10(10^((AC10-AC12-AC15)/10)+10^(AC13/10))<0,0,10*LOG10(10^((AC10-AC12-AC15)/10)+10^(AC13/10))))","v":72.266782770449126},86.002754624167494,89.000359130095035,80.00077520793468,57.048011611194525,44.320225041797052,55.008174715335123,63.000350993907688,64.000071278511427,{"$f":"IF(10*LOG10((10^(AC16/10))+(10^(AD16/10))+(10^(AE16/10))+(10^(AF16/10))+(10^(AG16/10))+(10^(AH16/10))+(10^(AI16/10))+(10^(AJ16/10))+(10^(AK16/10)))<20,\"<20\",10*LOG10((10^(AC16/10))+(10^(AD16/10))+(10^(AE16/10))+(10^(AF16/10))+(10^(AG16/10))+(10^(AH16/10))+(10^(AI16/10))+(10^(AJ16/10))+(10^(AK16/10))))","v":91.18919989649028}]
["t",20,null,"°C",{"$f":"IF(L17=1,\"teplota vzduchu (-50 až 200°C)\",\"zadejte teplotu v rozsahu -50 až 200°C\")","v":"teplota vzduchu (-50 až 200°C)"},null,null,null,null,null,null,{"$f":"IF(B17=\"\",0,IF(OR(B17<-50,B17>200),0,1))","v":1},null,"DC","dB",{"$f":"IF($L$26=0,\"\",AC18)","v":2.7332172295508741},3.9972453758325059,10.999640869904965,22.99922479206532,41.951988388805475,49.679774958202948,28.991825284664877,14.999649006092312,9.9999287214885726,{"$f":"IF(OR($L$26=0,$Y$16=\"<20\",$Y$12=\"<20\"),\"\",$Y$12-$Y$16)","v":23.931832379575255},null,"LWC-A","dBA",{"$f":"IF($L$26=0,0,IF((AC16+AC6)<0,0,AC16+AC6))","v":32.866782770449127},59.802754624167491,72.90035913009504,71.400775207934686,53.848011611194522,44.320225041797052,56.208174715335126,64.000350993907688,62.900071278511426,{"$f":"IF(10*LOG10((10^(AC17/10))+(10^(AD17/10))+(10^(AE17/10))+(10^(AF17/10))+(10^(AG17/10))+(10^(AH17/10))+(10^(AI17/10))+(10^(AJ17/10))+(10^(AK17/10)))<20,\"<20\",10*LOG10((10^(AC17/10))+(10^(AD17/10))+(10^(AE17/10))+(10^(AF17/10))+(10^(AG17/10))+(10^(AH17/10))+(10^(AI17/10))+(10^(AJ17/10))+(10^(AK17/10))))","v":75.956407112696496}]
["p",101325,null,"Pa",{"$f":"IF(L18=1,\"statický tlak v potrubí (98000 až 110000 Pa)\",\"zadejte statický tlak v rozsahu 98000 až 110000 Pa\")","v":"statický tlak v potrubí (98000 až 110000 Pa)"},null,null,null,null,null,null,{"$f":"IF(OR(B18<98000,B18>110000),0,1)","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"DC","dB",{"$f":"IF($L$26=0,0,IF($Y$10=\"L\",AC10-AC16,IF($Y$10=\"A\",AC11-AC17,\"\")))","v":2.7332172295508741},3.9972453758325059,10.999640869904965,22.99922479206532,41.951988388805475,49.679774958202948,28.991825284664877,14.999649006092312,9.9999287214885726,"-"]
["res",0.2,null,"%",{"$f":"IF(L19=1,\"rezerva na místní podmínky - procentuální navýšení ztráty\",\"rezerva musí být vždy kladné číslo\")","v":"rezerva na místní podmínky - procentuální navýšení ztráty"},null,null,null,null,null,null,{"$f":"IF(B19<0,0,1)","v":1},null,"Graf [svislá osa - dB / vodorovná osa - Hz]:"]
["ro",{"$f":"IF($L$26=0,\"\",$B$18/(287.15*(273.15+$B$17)))","v":1.2036989821185216},null,"kg/m3","hustota vzduchu",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Podmínky výběru"]
["S",{"$f":"IF($L$26=0,\"\",PI()/4*($B$13/1000)^2)","v":7.793113276311181E-2},null,"m2","plocha vstupního potrubí",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Typ","Vstup","Délka","Označení tlumiče",null,null,"Jádro","Vnější","Váha","Ksi","Cena","Příruba",31.5,63,125,250,500,1000,2000,4000,8000]
["Si",{"$f":"IF($L$26=0,\"\",PI()/4*($B$13^2-$AG$22^2)/1000000)","v":7.793113276311181E-2},null,"m2","volná průtočná plocha v tlumiči",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CONCATENATE(\"=\",B15)","v":"=GD"},{"$f":"B13","v":315},{"$f":"B14","v":2000},{"$f":"IF(ISERR(DGET(AA25:AU145,\"Označení tlumiče\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Označení tlumiče\",AA21:AC22))","v":"GD 315-2000"},null,null,{"$f":"IF(ISERR(DGET(AA25:AU145,\"Jádro\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Jádro\",AA21:AC22))","v":0},{"$f":"IF(ISERR(DGET(AA25:AU145,\"Vnější\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Vnější\",AA21:AC22))","v":500},{"$f":"IF(ISERR(DGET(AA25:AU145,\"Váha\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Váha\",AA21:AC22))","v":44.8},{"$f":"IF(ISERR(DGET(AA25:AU145,\"Ksi\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Ksi\",AA21:AC22))","v":0.18},{"$f":"IF(ISERR(DGET(AA25:AU145,\"Cena\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Cena\",AA21:AC22))","v":12235},{"$f":"IF(ISERR(DGET(AA25:AU145,\"Příruba\",AA21:AC22)),\"\",DGET(AA25:AU145,\"Příruba\",AA21:AC22))","v":1110},{"$f":"IF(ISERR(DGET(AA25:AU145,\"31,5\",AA21:AC22)),\"\",DGET(AA25:AU145,\"31,5\",AA21:AC22))","v":3},{"$f":"IF(ISERR(DGET(AA25:AU145,\"63\",AA21:AC22)),\"\",DGET(AA25:AU145,\"63\",AA21:AC22))","v":4},{"$f":"IF(ISERR(DGET(AA25:AU145,\"125\",AA21:AC22)),\"\",DGET(AA25:AU145,\"125\",AA21:AC22))","v":11},{"$f":"IF(ISERR(DGET(AA25:AU145,\"250\",AA21:AC22)),\"\",DGET(AA25:AU145,\"250\",AA21:AC22))","v":23},{"$f":"IF(ISERR(DGET(AA25:AU145,\"500\",AA21:AC22)),\"\",DGET(AA25:AU145,\"500\",AA21:AC22))","v":42},{"$f":"IF(ISERR(DGET(AA25:AU145,\"1000\",AA21:AC22)),\"\",DGET(AA25:AU145,\"1000\",AA21:AC22))","v":50},{"$f":"IF(ISERR(DGET(AA25:AU145,\"2000\",AA21:AC22)),\"\",DGET(AA25:AU145,\"2000\",AA21:AC22))","v":29},{"$f":"IF(ISERR(DGET(AA25:AU145,\"4000\",AA21:AC22)),\"\",DGET(AA25:AU145,\"4000\",AA21:AC22))","v":15},{"$f":"IF(ISERR(DGET(AA25:AU145,\"8000\",AA21:AC22)),\"\",DGET(AA25:AU145,\"8000\",AA21:AC22))","v":10}]
["w",{"$f":"IF($L$26=0,\"\",$B$12/3600/$B$21)","v":17.822003089711412},null,"m/s","rychlost proudění ve vstupním potrubí před tlumičem"]
["wi",{"$f":"IF($L$26=0,\"\",$B$12/3600/$B$22)","v":17.822003089711412},null,"m/s",{"$f":"IF(L24=1,\"rychlost proudění uvnitř v tlumiči\",\"rychlost proudění překračuje 25 m/s, zvolte větší dimenzi\")","v":"rychlost proudění uvnitř v tlumiči"},null,null,null,null,null,null,{"$f":"IF(B24=\"\",1,IF(B24<=25,1,0))","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Data katalog"]
["x",{"$f":"IF($L$26=0,\"\",$AJ$22)","v":0.18},null,"-","celkový součinitel tlakové ztráty tlumiče vztažený na plochu S",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Označení tlumiče",null,null,"Typ","Vstup","Jádro","Vnější","Délka","Váha","Ksi","Cena","Příruba",31.5,63,125,250,500,1000,2000,4000,8000]
["c",{"$f":"IF($L$26=0,\"\",(1.4*287.15*(273.15+$B$17))^0.5)","v":343.29175856696583},null,"m/s","rychlost zvuku ve vzduchu při teplotě t",null,null,null,null,null,null,{"$f":"L12*L13*L14*L15*L16*L17*L18*L19","v":1},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 100-1000",null,null,"GD",100,0,300,1000,12.5,0.56999999999999995,3565,580,5,6,18,30,38,50,50,42,24]
[null,null,null,null,null,null,null,null,null,null,null,"Výpočet je proveden na základě simulace CFD, odhad nepřesnosti ± 10%",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 125-1000",null,null,"GD",125,0,315,1000,13.5,0.36,3750,615,4,5,15,26,34,47,48,31,22]
["Vlastní hluk:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 140-1000",null,null,"GD",140,0,355,1000,16.100000000000001,0.28999999999999998,4240,645,4,5,14,25,33,46,46,29,20]
["f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"LWT-A",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 150-1000",null,null,"GD",150,0,355,1000,16.3,0.26,4500,690,4,5,13,24,32,45,44,27,18]
["LWT-Lin","dB",{"$f":"IF($L$26=0,\"\",AC13)","v":60.017808874809965},{"$f":"IF($L$26=0,\"\",AD13)","v":54.024157806065745},48.174854457459034,42.516726589776809,37.459647612648638,32.837806092016933,27.750971269105303,22.075328168559288,16.15177873892668,{"$f":"IF($L$26=0,\"\",AL14)","v":40.173267824161492},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 160-1000",null,null,"GD",160,0,355,1000,16.5,0.23,4715,705,4,5,11,23,31,44,42,26,15]
[null,null,null,null,null,null,null,null,null,null,null,"Nejistota výpočtu vlastního hluku ± 3 dB",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 180-1000",null,null,"GD",180,0,400,1000,18.5,0.21,5160,740,3,4,9,21,29,42,38,23,14]
["Útlum a váha kruhového tlumiče:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 200-1000",null,null,"GD",200,0,400,1000,18.8,0.18,5530,765,3,4,8,18,27,40,34,20,13]
["f","Hz",31.5,63,125,250,500,1000,2000,4000,8000,"M",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 224-1000",null,null,"GD",224,0,400,1000,18.899999999999999,0.15,6085,790,3,4,8,17,26,36,29,17,12]
["DT","dB",{"$f":"AC12","v":3},{"$f":"AD12","v":4},11,23,42,50,29,15,10,"kg/ks",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 250-1000",null,null,"GD",250,0,450,1000,21.5,0.12,6590,990,2,3,8,16,25,33,25,15,11]
["2sigR","dB",{"$f":"IF(C34=\"\",\"\",7)","v":7},{"$f":"IF(D34=\"\",\"\",6)","v":6},{"$f":"IF(E34=\"\",\"\",4)","v":4},{"$f":"IF(F34=\"\",\"\",4)","v":4},4,4,4,4,{"$f":"IF(K34=\"\",\"\",7)","v":7},{"$f":"IF(L26=0,\"\",AI22+2*B16*PI()*(B13+80)*80*1*7850/1000000000)","v":44.8},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD280-1000",null,null,"GD",280,0,500,1000,26.1,0.11,7190,1015,2,3,7,15,25,31,23,15,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 300-1000",null,null,"GD",300,0,500,1000,24.5,0.1,7545,1065,2,3,7,14,24,30,22,14,9]
["Závěrečné shrnutí výsledků:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 315-1000",null,null,"GD",315,0,500,1000,24.8,0.09,7760,1110,2,3,6,12,23,29,20,14,9]
["Označení tlumiče",null,null,{"$f":"IF($L$26=0,\"\",CONCATENATE(AD22,\".\",B16))","v":"GD 315-2000.0"},null,null,"Hmotnost tlumiče",null,null,{"$f":"IF($L$26=0,\"\",L35)","v":44.8},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 355-1000",null,null,"GD",355,0,560,1000,28.5,0.08,8980,1425,1,2,6,12,23,26,18,13,8]
["Nominální rozměr",null,null,{"$f":"IF(L26=0,\"\",AB22)","v":315},null,null,"Délka aktivní části",null,null,{"$f":"IF($L$26=0,\"\",AC22)","v":2000},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 400-1000",null,null,"GD",400,0,600,1000,30.5,0.06,9800,1735,1,2,5,11,23,25,16,12,7]
["Vnější průměr tlumiče",null,null,{"$f":"IF($L$26=0,\"\",AH22)","v":500},null,null,"Celková délka tlumiče",null,null,{"$f":"IF($L$26=0,\"\",J39+200)","v":2200},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 450-1000",null,null,"GD",450,0,630,1000,32.1,0.05,12545,2150,1,2,5,11,21,23,15,10,6]
["Brutto cena tlumiče (bez DPH, EXW Uhlířské Janovice)",null,null,null,null,null,null,null,null,{"$f":"IF($L$26=0,\"\",AK22+AL22*(2*B16))","v":12235},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 500-1000",null,null,"GD",500,0,710,1000,37.5,0.04,14880,2385,1,2,4,10,20,22,14,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 560-1000",null,null,"GD",560,0,800,1000,44.1,0.04,17885,2500,1,2,4,10,18,20,14,8,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 600-1000",null,null,"GD",600,0,800,1000,43.2,0.04,19040,2570,0,1,3,9,17,17,13,7,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 630-1000",null,null,"GD",630,0,900,1000,52,0.03,20335,3275,0,1,3,8,16,14,13,7,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 710-1000",null,null,"GD",710,0,900,1000,48.1,0.03,23070,3455,0,1,2,6,14,12,11,6,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 800-1000",null,null,"GD",800,0,1000,1000,65.099999999999994,0.03,25200,3640,0,1,2,5,12,10,9,6,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 900-1000",null,null,"GD",900,0,1120,1000,75.5,0.02,29875,10105,0,0,1,3,8,9,7,2,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 1000-1000",null,null,"GD",1000,0,1250,1000,87.2,0.02,32730,14250,0,0,0,1,4,5,4,1,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 100-1500",null,null,"GD",100,0,300,1500,17.5,0.84,4765,580,5,6,22,32,46,50,50,50,30]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 125-1500",null,null,"GD",125,0,315,1500,19,0.53,5020,615,5,6,18,27,42,50,50,40,27]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 140-1500",null,null,"GD",140,0,355,1500,22.1,0.44,5440,645,5,6,17,26,41,50,47,36,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 150-1500",null,null,"GD",150,0,355,1500,22.5,0.39,5715,690,5,6,16,25,41,50,46,32,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 160-1500",null,null,"GD",160,0,355,1500,22.8,0.35,6170,705,5,6,15,24,40,50,45,27,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 180-1500",null,null,"GD",180,0,400,1500,26.1,0.31,6805,740,4,5,13,22,38,49,40,24,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 200-1500",null,null,"GD",200,0,400,1500,26.3,0.27,7185,765,4,5,11,21,37,48,35,22,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 224-1500",null,null,"GD",224,0,400,1500,26.5,0.22,7930,790,3,4,11,21,37,44,31,18,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 250-1500",null,null,"GD",250,0,450,1500,30.5,0.19,8460,990,3,4,11,21,37,41,27,15,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 280-1500",null,null,"GD",280,0,500,1500,35.1,0.16,9225,1015,3,4,11,19,34,41,25,15,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 300-1500",null,null,"GD",300,0,500,1500,34.5,0.14000000000000001,9760,1065,2,3,10,17,31,41,24,14,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 315-1500",null,null,"GD",315,0,500,1500,34.799999999999997,0.13,10055,1110,2,3,9,16,31,41,23,14,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 355-1500",null,null,"GD",355,0,560,1500,40.200000000000003,0.11,11655,1425,2,3,8,15,30,36,19,13,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 400-1500",null,null,"GD",400,0,600,1500,43.1,0.09,12555,1735,2,3,7,15,30,31,16,12,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 450-1500",null,null,"GD",450,0,630,1500,45.1,0.08,15625,2150,1,2,6,15,30,29,15,10,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 500-1500",null,null,"GD",500,0,710,1500,53.1,0.06,18195,2385,1,2,6,14,29,27,14,8,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 560-1500",null,null,"GD",560,0,800,1500,62,0.06,21590,2500,1,2,5,14,29,25,14,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 600-1500",null,null,"GD",600,0,800,1500,65,0.06,23515,2570,1,2,5,13,28,24,13,7,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 630-1500",null,null,"GD",630,0,900,1500,73.5,0.04,24930,3275,1,2,5,12,28,23,13,7,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 710-1500",null,null,"GD",710,0,900,1500,68.2,0.04,27930,3455,1,2,4,11,27,21,11,6,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 800-1500",null,null,"GD",800,0,1000,1500,91.2,0.04,30620,3640,1,2,4,11,26,20,9,6,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 900-1500",null,null,"GD",900,0,1120,1500,105.5,0.03,39610,10105,0,1,3,8,20,16,6,4,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 1000-1500",null,null,"GD",1000,0,1250,1500,121.5,0.03,43135,14250,0,0,1,4,10,8,3,2,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 100-2000",null,null,"GD",100,0,300,2000,23,1.1299999999999999,5915,580,6,7,28,41,50,50,50,50,39]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 125-2000",null,null,"GD",125,0,315,2000,24.5,0.72,6250,615,6,7,23,35,50,50,50,50,35]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 140-2000",null,null,"GD",140,0,355,2000,29.1,0.57999999999999996,6670,645,6,7,21,33,50,50,50,45,31]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 150-2000",null,null,"GD",150,0,355,2000,29.3,0.52,7190,690,6,7,20,32,50,50,50,40,28]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 160-2000",null,null,"GD",160,0,355,2000,29.5,0.48,7555,705,6,7,19,31,50,50,50,35,24]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 180-2000",null,null,"GD",180,0,400,2000,34.1,0.41,8285,740,5,6,17,29,48,50,47,31,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 200-2000",null,null,"GD",200,0,400,2000,34.5,0.35,8760,765,5,6,16,27,48,50,45,28,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 224-2000",null,null,"GD",224,0,400,2000,35.5,0.28999999999999998,9575,790,4,5,15,27,47,50,37,23,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 250-2000",null,null,"GD",250,0,450,2000,39.1,0.26,10230,990,4,5,14,27,46,50,35,19,15]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 280-2000",null,null,"GD",280,0,500,2000,45.1,0.21,11050,1015,4,5,13,25,44,50,33,17,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 300-2000",null,null,"GD",300,0,500,2000,44.5,0.19,11655,1065,3,4,12,24,43,50,31,16,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 315-2000",null,null,"GD",315,0,500,2000,44.8,0.18,12235,1110,3,4,11,23,42,50,29,15,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 355-2000",null,null,"GD",355,0,560,2000,51.5,0.15,14025,1425,3,4,10,21,41,45,24,14,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 400-2000",null,null,"GD",400,0,600,2000,55.5,0.13,15300,1735,2,3,9,20,41,40,20,13,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 450-2000",null,null,"GD",450,0,630,2000,58.1,0.11,18455,2150,2,3,8,19,40,37,19,11,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 500-2000",null,null,"GD",500,0,710,2000,68.2,0.08,21510,2385,1,2,7,18,39,35,19,9,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 560-2000",null,null,"GD",560,0,800,2000,80.3,0.08,25820,2500,1,2,7,17,38,33,17,9,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 600-2000",null,null,"GD",600,0,800,2000,87.5,0.08,28085,2570,1,2,6,16,37,31,16,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 630-2000",null,null,"GD",630,0,900,2000,94.2,0.05,29550,3275,1,2,6,15,36,29,14,8,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 710-2000",null,null,"GD",710,0,900,2000,97.5,0.05,33225,3455,1,2,6,14,34,27,12,7,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 800-2000",null,null,"GD",800,0,1000,2000,117.2,0.05,36070,3640,1,2,5,14,33,26,10,6,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 900-2000",null,null,"GD",900,0,1120,2000,135.1,0.04,49175,10105,0,1,4,10,23,18,8,5,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GD 1000-2000",null,null,"GD",1000,0,1250,2000,156.6,0.04,53540,14250,0,1,2,5,12,9,4,3,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 200-1000",null,null,"GDE",200,120,400,1000,25.1,1.46,6530,765,6,7,12,22,40,50,50,50,46]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 224-1000",null,null,"GDE",224,120,400,1000,25.5,0.87,7190,790,5,6,11,19,35,48,50,50,41]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 250-1000",null,null,"GDE",250,120,450,1000,29.2,0.56999999999999995,7635,990,4,5,10,17,30,47,50,50,36]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 280-1000",null,null,"GDE",280,190,500,1000,34.5,2.2799999999999998,8450,1015,4,5,10,16,29,46,48,47,33]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 300-1000",null,null,"GDE",300,190,500,1000,34.6,1.53,8945,1065,3,4,9,15,28,45,46,44,30]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 315-1000",null,null,"GDE",315,190,500,1000,34.799999999999997,1.4,9305,1110,3,4,9,15,27,44,45,39,27]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 355-1000",null,null,"GDE",355,240,560,1000,39.5,2.44,10685,1425,3,4,8,14,26,43,42,34,24]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 400-1000",null,null,"GDE",400,240,600,1000,43.5,1.1200000000000001,11655,1735,3,3,7,13,25,40,38,29,21]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 450-1000",null,null,"GDE",450,290,630,1000,47,1.51,14745,2150,2,3,7,12,24,39,35,26,18]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 500-1000",null,null,"GDE",500,290,710,1000,55.1,0.96,17170,2385,1,2,6,12,23,38,33,24,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 560-1000",null,null,"GDE",560,390,800,1000,66.099999999999994,2.42,21575,2500,1,2,6,11,22,36,31,21,15]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 600-1000",null,null,"GDE",600,390,800,1000,64.5,1.45,22790,2570,1,2,5,11,21,35,30,20,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 630-1000",null,null,"GDE",630,390,900,1000,75,1.45,23775,3275,1,2,5,11,21,34,29,19,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 710-1000",null,null,"GDE",710,390,900,1000,81.5,0.52,27130,3455,1,2,4,10,20,30,22,14,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 800-1000",null,null,"GDE",800,490,1000,1000,94.5,1.1299999999999999,29680,3640,1,2,2,8,15,24,18,10,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 900-1000",null,null,"GDE",900,590,1120,1000,109.5,1.21,41120,10105,1,1,2,7,12,20,15,8,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 1000-1000",null,null,"GDE",1000,690,1250,1000,125.5,2.14,47835,14250,1,1,1,6,10,15,10,6,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 200-1500",null,null,"GDE",200,120,400,1500,35.5,2.0099999999999998,8545,765,8,9,16,26,45,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 224-1500",null,null,"GDE",224,120,400,1500,35.799999999999997,1.36,9225,790,7,8,15,24,42,50,50,50,47]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 250-1500",null,null,"GDE",250,120,450,1500,40.5,0.83,9835,990,6,7,14,22,41,50,50,50,44]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 280-1500",null,null,"GDE",280,190,500,1500,48.5,2.78,10975,1015,6,7,14,21,39,50,50,50,40]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 300-1500",null,null,"GDE",300,190,500,1500,48.6,1.75,11470,1065,6,7,13,20,38,50,50,50,37]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 315-1500",null,null,"GDE",315,190,500,1500,48.8,1.49,12110,1110,6,7,12,20,37,50,50,50,34]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 355-1500",null,null,"GDE",355,240,560,1500,55,2.74,13820,1425,5,6,11,18,34,50,50,45,30]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 400-1500",null,null,"GDE",400,240,600,1500,61.1,1.21,15170,1735,5,6,10,17,33,50,50,40,26]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 450-1500",null,null,"GDE",450,290,630,1500,66.3,1.83,18455,2150,4,5,9,16,31,50,50,36,23]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 500-1500",null,null,"GDE",500,290,710,1500,76.2,1.22,21415,2385,4,5,9,16,30,50,50,33,21]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 560-1500",null,null,"GDE",560,390,800,1500,93.5,2.71,25820,2500,3,4,8,15,30,50,48,29,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 600-1500",null,null,"GDE",600,390,800,1500,97,1.56,28020,2570,3,4,8,14,29,50,46,27,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 630-1500",null,null,"GDE",630,390,900,1500,106.2,1.56,29650,3275,3,4,8,14,29,50,44,26,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 710-1500",null,null,"GDE",710,390,900,1500,110.5,0.79,33225,3455,3,4,7,13,28,50,41,23,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 800-1500",null,null,"GDE",800,490,1000,1500,133.5,1.26,36730,3640,2,3,6,13,26,49,37,20,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 900-1500",null,null,"GDE",900,590,1120,1500,156.19999999999999,1.84,54715,10105,2,2,4,10,20,39,29,16,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 1000-1500",null,null,"GDE",1000,690,1250,1500,181.5,2.31,63440,14250,1,2,3,6,10,19,14,8,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 200-2000",null,null,"GDE",200,120,400,2000,45,2.5,10580,765,9,10,19,31,50,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 224-2000",null,null,"GDE",224,120,400,2000,45.4,1.78,11420,790,8,9,18,28,50,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 250-2000",null,null,"GDE",250,120,450,2000,52.2,1.05,11990,990,7,8,17,26,49,50,50,50,50]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 280-2000",null,null,"GDE",280,190,500,2000,62.5,3.25,13500,1015,7,8,17,25,46,50,50,50,48]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 300-2000",null,null,"GDE",300,190,500,2000,62.7,1.97,14360,1065,7,8,15,24,45,50,50,50,44]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 315-2000",null,null,"GDE",315,190,500,2000,62.9,1.57,14880,1110,7,8,14,24,44,50,50,50,40]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 355-2000",null,null,"GDE",355,240,560,2000,70.5,3,17010,1425,6,7,13,21,40,50,50,50,36]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 400-2000",null,null,"GDE",400,240,600,2000,78.5,1.28,18665,1735,6,7,12,20,39,50,50,48,31]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 450-2000",null,null,"GDE",450,290,630,2000,85.5,2.11,22665,2150,5,6,11,19,37,50,50,43,27]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 500-2000",null,null,"GDE",500,290,710,2000,98.1,1.48,25620,2385,5,6,11,19,36,50,50,39,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 560-2000",null,null,"GDE",560,390,800,2000,120.5,2.97,31225,2500,4,5,10,18,36,50,50,35,22]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 600-2000",null,null,"GDE",600,390,800,2000,127.5,1.67,33800,2570,4,5,10,17,35,50,50,32,20]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 630-2000",null,null,"GDE",630,390,900,2000,137,1.67,35495,3275,4,5,10,17,35,50,50,31,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 710-2000",null,null,"GDE",710,390,900,2000,139.5,1.02,39810,3455,3,4,8,15,33,50,49,28,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 800-2000",null,null,"GDE",800,490,1000,2000,172.5,1.44,43745,3640,3,4,7,15,31,50,44,24,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 900-2000",null,null,"GDE",900,590,1120,2000,202.5,2.21,68310,10105,3,4,7,14,29,50,41,20,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"GDE 1000-2000",null,null,"GDE",1000,690,1250,2000,237,2.63,79050,14250,3,4,7,13,27,50,40,19,12]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Vlastní hluk - typy GD / GDE"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Q","d","dj","t","p","typ","S","Si","w","wi","c","Ma","H","delta","Wo","B",31.5,63,125,250,500,1000,2000,4000,8000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"m3/h","mm","mm","°C","Pa","-","m2","m2","m/s","m/s","m/s","m/s","m","-","W","-","dB","dB","dB","dB","dB","dB","dB","dB","dB"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"B12","v":5000},{"$f":"B13","v":315},{"$f":"AG22","v":0},{"$f":"B17","v":20},{"$f":"B18","v":101325},{"$f":"B15","v":"GD"},{"$f":"PI()*AB150^2/4/1000000","v":7.793113276311181E-2},{"$f":"PI()/4*(AB150^2-AC150^2)/1000000","v":7.793113276311181E-2},{"$f":"AA150/3600/AG150","v":17.822003089711412},{"$f":"AA150/3600/AH150","v":17.822003089711412},{"$f":"(1.4*287.15*(AD150+273.15))^0.5","v":343.29175856696583},{"$f":"AJ150/AK150","v":5.1915033335223161E-2},{"$f":"IF(AF150=\"GD\",AB150/1000,IF(AF150=\"GDE\",(AB150-AC150)/2000))","v":0.315},0.02,1,48,{"$f":"$AP150+(10*LOG10($AE150*$AK150*$AH150/$AO150)+60*LOG10($AL150)+10*LOG10(1+($AK150/2/AQ$148/$AM150)^2)-10*LOG10(1+(AQ$148*$AN150/$AJ150)^2))","v":60.017808874809965},{"$f":"$AP150+(10*LOG10($AE150*$AK150*$AH150/$AO150)+60*LOG10($AL150)+10*LOG10(1+($AK150/2/AR$148/$AM150)^2)-10*LOG10(1+(AR$148*$AN150/$AJ150)^2))","v":54.024157806065745},48.174854457459034,42.516726589776809,37.459647612648638,32.837806092016933,27.750971269105303,22.075328168559288,16.15177873892668]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Aktualizace SW"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3.0","2023-03-19",null,"Změna tisku na 1A naležato, změna cen, roztažení poznámek, změna grafiky v záhlaví, aktualizace čísla verze."]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"5.0","2026-03-13",null,"Aktualizace cen na rok 2026. Navýšení +5% oproti starému ceníku."]